## 9-Mar-11
AguaClara Lab |  | Notes:
2011-03-09 |  | Dosing with room temperature water
1:30 PM - 2:40 PM |  | 1 small diameter tube
Elevation Setting (cm) | Dosing Time (s) | Expected Volume dosed (mL) | Expected Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Percent Error | Mult | Mult*Q.Exp | Percent Error
1 | 100 | 15.6 | 0.156 | 12.5 | 0.125 | 24.8 | 0.7538 | 0.11759 | 0.062993
2 | 100 | 31.2 | 0.312 | 28 | 0.28 | 11.4286 | 0.7538 | 0.23518 | 0.19055
3 | 100 | 46.8 | 0.468 | 42.5 | 0.425 | 10.1176 | 0.7538 | 0.35278 | 0.20473
4 | 100 | 62.4 | 0.624 | 57 | 0.57 | 9.4737 | 0.7538 | 0.47037 | 0.21181
5 | 100 | 78 | 0.78 | 67.5 | 0.675 | 15.5556 | 0.7538 | 0.58796 | 0.14803
6 | 100 | 93.6 | 0.936 | 77.5 | 0.775 | 20.7742 | 0.7538 | 0.70555 | 0.098426
7 | 100 | 109.2 | 1.092 | 88 | 0.88 | 24.0909 | 0.7538 | 0.82315 | 0.069067
8 | 100 | 124.8 | 1.248 | 98.5 | 0.985 | 26.7005 | 0.7538 | 0.94074 | 0.047048
9 | 60 | 84.24 | 1.404 | 63.5 | 1.0583 | 32.6614 | 0.7538 | 1.0583 | 9.1351e-07
10 | 60 | 93.6 | 1.56 | 69.25 | 1.1542 | 35.1625 | 0.7538 | 1.1759 | 0.018503
11 | 60 | 102.96 | 1.716 | 74.5 | 1.2417 | 38.2013 | 0.7538 | 1.2935 | 0.040085
12 | 60 | 112.32 | 1.872 | 80.25 | 1.3375 | 39.9626 | 0.7538 | 1.4111 | 0.052164
13 | 60 | 121.68 | 2.028 | 85 | 1.4167 | 43.1529 | 0.7538 | 1.5287 | 0.073288
14 | 60 | 131.04 | 2.184 | 91 | 1.5167 | 44 | 0.7538 | 1.6463 | 0.078739
15 | 60 | 140.4 | 2.34 | 96.5 | 1.6083 | 45.4922 | 0.7538 | 1.7639 | 0.088188
16 | 45 | 112.32 | 2.496 | 76 | 1.6889 | 47.7895 | 0.7538 | 1.8815 | 0.10236
17 | 45 | 119.34 | 2.652 | 79.5 | 1.7667 | 50.1132 | 0.7538 | 1.9991 | 0.11626
18 | 45 | 126.36 | 2.808 | 82 | 1.8222 | 54.0976 | 0.7538 | 2.1167 | 0.13911
19 | 45 | 133.38 | 2.964 | 85.5 | 1.9 | 56 | 0.7538 | 2.2343 | 0.14961
20 | 45 | 140.4 | 3.12 | 89 | 1.9778 | 57.7528 | 0.7538 | 2.3518 | 0.15905
[8 empty] | Sum | 2.05

## 13-Mar-11
AguaClara Lab |  | Notes: |  | graduated cylinder mass | 42 | g
2011-03-13 |  | Dosing with room temperature water
21:00 |  | 1 small diameter tube
Elevation Setting (cm) | Dosing Time (s) | Expected Volume dosed (mL) | Expected Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Percent Error | Multiplier | Mult*Q.Exp | Percent Error
1 | 100 | 15.6 | 0.156 | 12 | 0.12 | 30 | 0.80614 | 0.12576 | 0.045783
2 | 100 | 31.2 | 0.312 | 28 | 0.28 | 11.4286 | 0.80614 | 0.25152 | 0.11325
3 | 100 | 46.8 | 0.468 | 43 | 0.43 | 8.8372 | 0.80614 | 0.37727 | 0.13976
4 | 100 | 62.4 | 0.624 | 55 | 0.55 | 13.4545 | 0.80614 | 0.50303 | 0.093373
5 | 100 | 78 | 0.78 | 68 | 0.68 | 14.7059 | 0.80614 | 0.62879 | 0.081446
6 | 100 | 93.6 | 0.936 | 80 | 0.8 | 17 | 0.80614 | 0.75455 | 0.060241
7 | 100 | 109.2 | 1.092 | 93 | 0.93 | 17.4194 | 0.80614 | 0.8803 | 0.056454
8 | 100 | 124.8 | 1.248 | 105 | 1.05 | 18.8571 | 0.80614 | 1.0061 | 0.043675
9 | 60 | 84.24 | 1.404 | 69 | 1.15 | 22.087 | 0.80614 | 1.1318 | 0.016064
10 | 60 | 93.6 | 1.56 | 76 | 1.2667 | 23.1579 | 0.80614 | 1.2576 | 0.0072289
11 | 60 | 102.96 | 1.716 | 83 | 1.3833 | 24.0482 | 0.80614 | 1.3833 | 9.7552e-09
12 | 60 | 112.32 | 1.872 | 88 | 1.4667 | 27.6364 | 0.80614 | 1.5091 | 0.028112
13 | 60 | 121.68 | 2.028 | 94 | 1.5667 | 29.4468 | 0.80614 | 1.6348 | 0.041705
14 | 60 | 131.04 | 2.184 | 100 | 1.6667 | 31.04 | 0.80614 | 1.7606 | 0.053356
15 | 60 | 140.4 | 2.34 | 106 | 1.7667 | 32.4528 | 0.80614 | 1.8864 | 0.063454
16 | 45 | 112.32 | 2.496 | 83 | 1.8444 | 35.3253 | 0.80614 | 2.0121 | 0.083333
17 | 45 | 119.34 | 2.652 | 86 | 1.9111 | 38.7674 | 0.80614 | 2.1379 | 0.10607
18 | 45 | 126.36 | 2.808 | 89 | 1.9778 | 41.9775 | 0.80614 | 2.2636 | 0.12628
19 | 45 | 133.38 | 2.964 | 94 | 2.0889 | 41.8936 | 0.80614 | 2.3894 | 0.12577
20 | 45 | 140.4 | 3.12 | 97 | 2.1556 | 44.7423 | 0.80614 | 2.5152 | 0.14297
[8 empty] | sum | 1.4283 | Min SE

## 17-Mar-11
AguaClara Lab |  | Notes: |  | graduated cylinder mass | 42 | g
2011-03-17 |  | Dosing with room temperature water
21:00 |  | 2 small diameter tubes
Elevation Setting (cm) | Dosing Time (s) | Expected Volume dosed (mL) | Expected Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Percent Error | Mult | Mult*Q.Exp | Percent Error
1 | 60 | 18.72 | 0.312 | 23 | 0.38333 | -18.6087 | 0.84402 | 0.26334 | 0.45568
2 |  | 0 | 0.624 |  |  | #DIV/0!
3 |  | 0 | 0.936 |  |  | #DIV/0!
4 |  | 0 | 1.248 |  |  | #DIV/0!
5 | 60 | 93.6 | 1.56 | 93 | 1.55 | 0.64516 | 0.84402 | 1.3167 | 0.17721
6 |  | 0 | 1.872 |  |  | #DIV/0!
7 |  | 0 | 2.184 |  |  | #DIV/0!
8 |  | 0 | 2.496 |  |  | #DIV/0!
9 |  | 0 | 2.808 |  |  | #DIV/0!
10 | 60 | 187.2 | 3.12 | 158 | 2.6333 | 18.481 | 0.84402 | 2.6334 | 8.0958e-06
11 |  | 0 | 3.432 |  |  | #DIV/0!
12 |  | 0 | 3.744 |  |  | #DIV/0!
13 |  | 0 | 4.056 |  |  | #DIV/0!
14 |  | 0 | 4.368 |  |  | #DIV/0!
15 | 60 | 280.8 | 4.68 | 217 | 3.6167 | 29.4009 | 0.84402 | 3.95 | 0.084396
16 |  | 0 | 4.992 |  |  | #DIV/0!
17 |  | 0 | 5.304 |  |  | #DIV/0!
18 |  | 0 | 5.616 |  |  | #DIV/0!
19 |  | 0 | 5.928 |  |  | #DIV/0!
20 | 60 | 374.4 | 6.24 | 258 | 4.3 | 45.1163 | 0.84402 | 5.2667 | 0.18355
[8 empty] | Sum | 0.90084

## 15-Mar-11
AguaClara Lab |  | Notes: |  | graduated cylinder mass | 196 | g
2011-03-15 |  | Dosing with room temperature water
21:00 |  | 3 small diameter tubes
Elevation Setting (cm) | Dosing Time (s) | Expected Volume dosed (mL) | Expected Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Percent Error | Mult | Mult*Q.Exp | Percent Error
1 | 60 | 29.94 | 0.499 | 26 | 0.43333 | 15.1538 | 0.76122 | 0.37985 | 0.14081
2 |  | 0 | 0.998
3 |  | 0 | 1.497
4 |  | 0 | 1.997
5 | 60 | 149.76 | 2.496 | 125 | 2.0833 | 19.808 | 0.76122 | 1.9 | 0.096491
6 |  | 0 | 2.995
7 |  | 0 | 3.494
8 |  | 0 | 3.993
9 |  | 0 | 4.492
10 | 60 | 299.52 | 4.992 | 228 | 3.8 | 31.3684 | 0.76122 | 3.8 | 2.4533e-08
11 |  | 0 | 5.491
12 |  | 0 | 5.99
13 |  | 0 | 6.489
14 |  | 0 | 6.988
15 | 60 | 449.22 | 7.487 | 311 | 5.1833 | 44.4437 | 0.76122 | 5.6992 | 0.090522
16 |  | 0 | 7.987
17 |  | 0 | 8.486
18 |  | 0 | 8.985
19 |  | 0 | 9.484
20 | 60 | 598.98 | 9.983 | 370 | 6.1667 | 61.8865 | 0.76122 | 7.5992 | 0.18852
[8 empty] | Sum | 0.51634

## 10-Apr-11
AguaClara Lab |  | Notes: L = 10.013 ft. D = 0.125in |  | graduated cylinder mass | 42 | [6 empty] | g
2011-04-10 |  | Dosing with room temperature water
0:42 |  | 1 small diameter tubes
|  |  |  | #1 |  | #2 |  | #3 |  |  |  |  | expected |  | actual
Elevation Setting (cm) | Dosing Time (s) | Expected Volume dosed (mL) | Expected Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Avg. Actual Vol dosed (mL) | Avg. Actual Flow Rate (mL/s) | Percent Error | Q.linear | Error | Q.linear | Error
0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
1 | 60 | [10 empty] | 0
2
3
4 | 60 |  | 0.316 | 19 | 0.31667 | 18 | 0.3 | 19 | 0.31667 | 18.6667 | 0.31111 | 1.5439 | 0.0632 | -0.2528 | 0.062222 | -0.24889
5
6
7
8 | 60 |  | 0.623 | 37 | 0.61667 | 37 | 0.61667 | 37 | 0.61667 | 37 | 0.61667 | 1.027 | 0.2492 | -0.3738 | 0.24667 | -0.37
9
10
11
12 | 60 |  | 0.923 | 55 | 0.91667 | 54 | 0.9 | 54 | 0.9 | 54.3333 | 0.90556 | 1.903 | 0.5538 | -0.3692 | 0.54333 | -0.36222
13
14
15
16 | 60 |  | 1.215 | 69 | 1.15 | 70 | 1.1667 | 69 | 1.15 | 69.3333 | 1.1556 | 5.1691 | 0.972 | -0.243 | 0.92444 | -0.23111
17
18
19
20 | 60 | 90 | 1.5 | 84 | 1.4 | 83 | 1.3833 | 83 | 1.3833 | 83.3333 | 1.3889 | 7.9365 | 1.5 | 0 | 1.3889 | 0

## 10-Apr-11 (2)
AguaClara Lab |  | Notes: L = 9.675ft. D = 0.124in |  | graduated cylinder mass | 42 | [6 empty] | g
2011-04-10 |  | Dosing with room temperature water
0:42 |  | 1 small diameter tubes
|  |  |  | #1 |  | #2 |  | #3
Elevation Setting (cm) | Dosing Time (s) | Expected Volume dosed (mL) | Expected Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Actual Volume dosed (mL) | Actual Flow Rate (mL/s) | Avg. Actual Vol dosed (mL) | Avg. Actual Flow Rate (mL/s) | Percent Error | Q.linear | Error
0 | 60 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | [12 empty] | 0
2 | [12 empty] | 0
3 | [12 empty] | 0
4 | 60 |  | 0.317 | 18 | 0.3 | 19 | 0.31667 | 20 | 0.33333 | 19 | 0.31667 | 0.11111 | 0.063333 | -0.25333
5 | [12 empty] | 0
6 | [12 empty] | 0
7 | [12 empty] | 0
8 | 60 |  | 0.624 | 38 | 0.63333 | 38 | 0.63333 | 45 | 0.64286 | 40.3333 | 0.67222 | -7.614 | 0.26889 | -0.40333
9 | [12 empty] | 0
10 | [12 empty] | 0
11 | [12 empty] | 0
12 | 60 |  | 0.924 | 56 | 0.93333 | 55 | 0.91667 | 56 | 0.93333 | 55.6667 | 0.92778 | -0.40476 | 0.55667 | -0.37111
13 | [12 empty] | 0
14 | [12 empty] | 0
15 | [12 empty] | 0
16 | 60 |  | 1.216 | 71 | 1.1833 | 72 | 1.2 | 72 | 1.2 | 71.6667 | 1.1944 | 1.8216 | 0.95556 | -0.23889
17 | [12 empty] | 0
18 | [12 empty] | 0
19 | [12 empty] | 0
20 | 60 | 90 | 1.5 | 86 | 1.4333 | 87 | 1.45 | 87 | 1.45 | 86.6667 | 1.4444 | 3.876 | 1.4444 | 0

## MaxError
Qexpected | Qlinear | Error